## Process
International phasing |  |  | BASICS | [5 empty] | DESIGN | [30 empty] | CONSTRUCTION | [7 empty] | OPERATION
Example national phasing |  |  | BASICS | [5 empty] | PRE DESIGN | [9 empty] | CONCEPT DESIGN | [9 empty] | DESIGN DEVELOPMENT | [7 empty] | BUILDING DOCS |  |  | NEGOTIATING CONTRACTING |  | EXECUTION & COMMISSIONING | [5 empty] | OPERATION
W O R K F L O W | A |  |  | B010 |  |  | B020 |  |  |  | A010 |  |  |  | A020 |  |  | Transition |  |  | A030 |  |  |  | A040 |  |  | Transition |  |  | A050 |  |  | A060 |  |  |  | A070 | Transition | [6 empty] | A080 |  |  | A090 | A100
|  |  |  | - Project brief - Objectives - Background - Influences |  |  | - Site inspection - Site analysis |  |  |  | Rough cost estimate |  |  |  | Consider Building codes, regulations and industry standards | [5 empty] | - Review goals and requirements - Qualified cost estimation |  |  |  | - Calculations - Simulations - Quantifications | [5 empty] | - Life cycle analysis - Cost calculation |  |  | - Detailed calculations - Simulation |  |  |  | Construction strategies | [7 empty] | Commissioning plan for energy related |  |  | Operation strategies | Management and Maintenance plan
|  |  |  | Cl, AR |  |  | AR, ES, CS, LD, ID, DF |  |  |  | AR, RO, OS, CS, C |  |  |  | AR, EP, ME | [5 empty] | AR, DV, EP |  |  |  | AR, EP, ES | [5 empty] | AR, BO |  |  | ES, AR, SE, DS, LS |  |  |  | AR,SE,EP | [7 empty] | AR, ME, DS, LS, CS |  |  | AR, BO, CL, QS | BO, MS, BM, QS
|  |  |  | 409030 |  |  | 409030 |  |  |  | 213011,308020,207037 |  |  |  | 213061, 103007, 104056, 103018 | [5 empty] | 308020 |  |  |  | 308020,207037,308054,313063 | [5 empty] | 308020,207037 |  |  | 313063, 308054 |  |  |  | 103018,213032,101053 | [7 empty] | 308034,300035,308045,308048,308049 |  |  | 308034,300035,308045,300067 | 312028, 308049, 308048, 308045
|  |  |  | T01301,T01303 |  |  | T01303 |  |  |  | T03101,T03102, T042510, T042511, T042512 |  |  |  | T02101 | [5 empty] | T02203,T04102,T04101 |  |  |  | T04271,T04272 | [5 empty] | T04104 |  |  | T04252 |  |  |  | T01110 | [7 empty] | 0 |  |  | 0 | 0
B
[10 empty] | B030 | [5 empty] | B040 |  |  |  | B050 | [5 empty] | B060 |  |  |  | B070 |  |  |  |  | B080 |  |  | B090 |  |  | B100 |  | B110 |  | B120
[10 empty] | Investigation on: - Urban integration - Proportion - Site development |  |  |  | Predesign loop |  | General approach for energy supply and systems |  |  |  | Check Interfaces: - Proportions - Multifunctionality - Flexibility |  |  |  | Concept design loop |  | Design and gross sizing of system solutions |  |  |  | Modular tuning of: - Space use - Construction elements |  |  | Design development loop |  | - Optimise system solutions - Final sizing - System operation |  |  | Environmental criteria and specs for tender |  |  | Requirements upon builders and suppliers, Call for tender |  | Implementation of necessary changes |  | Analyse and assess impact caused by project change
[5 empty] | from demand to goals | [5 empty] | from shape to structure | [9 empty] | from structure to systems | [9 empty] | from systems to components
[10 empty] | AR, RO, LD | [5 empty] | AR, EP, DF, BS, ES, DS |  |  |  | AR, SE, O, QS, TS, CS, EL | [5 empty] | DT, CL |  |  |  | AR, PM |  |  |  |  | AR, EP, ME, QS |  |  | AR, EP, DF, MS, AS, SS, BO |  |  | AR, AS, SS, CS, BS |  | AR, PM, CL |  | AR, QS, CL, DF
[10 empty] | 312050 | [5 empty] | 213011,111014,308020,213032,213043,308049,308054,308059,213061,313063 |  |  |  | 213046 | [5 empty] | 213011,111014,308020,213043,308054,313063 |  |  |  | 111002 |  |  |  |  | 112036,313063 |  |  | 103018,308020,101053,308059 |  |  | 402004,103018,213032,101053,308059,308062 |  | 409055,300056 |  | 409055,300056
[10 empty] | T01301,T02203 | [5 empty] | T02101,T02103 |  |  |  | 0 | [5 empty] | T04252 |  |  |  | 0 |  |  |  |  | T04252 |  |  | T02205,T02206,T02203,T02104 |  |  | 0 |  | 0 |  | 0
| C | Main activities (core team) | [9 empty] | C030 | [9 empty] | C120
|  |  |  | C010 |  |  | C020 |  |  |  |  | - General dispositions mass/functions - Horizontal/vertical development - Building periphery | [9 empty] | - Building and energy system - Spatial structure and Construction - Envelope, daylighting, solar - Traffic and HVAC systems | [9 empty] | C040 | [5 empty] | C050 |  |  | C060 |  |  | C070 |  | C080 |  |  | C090 |  | C100 |  |  | C110
|  |  |  | Programme demand and requirements |  |  | Feasibility studies | [24 empty] | - System integration - Selection of building components and materials | [5 empty] | Construction documents |  |  | Bidding |  |  | Construction supervision, Cost control, Quality assurance |  | Final commissioning |  |  | Operation manuals |  | Management, Control, Optimisation |  |  | Basics for retrofit design
[12 empty] | Cl, AR, EP, DF | [9 empty] | Cl, AR, EP, DF
|  |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  |  |  |  | 413016,313058,313065 | [9 empty] | 413016,313058,313065 | [9 empty] | DT, AR, SE, EP, ME, DF | [5 empty] | AR, SE, ME |  |  | AR, ME, EL, BS, MS, AS,CS, SS |  |  | AS, CS, SS |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF
|  |  |  | 101012,312050 |  |  | 312050,313065 |  |  |  |  | T01106, T01108, T01301 | [9 empty] | T01106, T01108, T01301 | [9 empty] | 413016,313058,313065, 112036 | [5 empty] | 413016,103018,112036,207037,308038,208039,312050,313058,308062,313065,300066 |  |  | 402004,103018,308020,213032,308062, 112036 |  |  | 308038,208039 |  | 308034,300035,308048,308049,313057 |  |  | 100021,308044,308045,400064,300067 |  | 100021,308044,409055,300056,400064,300067 |  |  | 100021,409055,300056
|  |  |  | 0 |  |  | 0 | [24 empty] | T04261,T04262 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0
D
[6 empty] | D010 |  |  |  | D020 |  |  | D030 |  |  | D040 |  |  |  | D050 |  |  | D060 | [6 empty] | D070 |  |  | D080 | [7 empty] | D090 |  | D100 |  | D110 |  |  |  | D120 | D130 |  | D140
[6 empty] | First design advice |  |  |  | Set up design team (alternatives) |  |  | Call in expert (e.g. jury, …) |  |  | Design'alternatives |  |  |  | Set up / complete 'design team |  |  | Call in expert | [6 empty] | Complete 'design team |  |  | Call in expert | [7 empty] | Negotiation |  | Identify and eliminate deficiencies |  | Operational, functional and energy performance checks |  |  |  | User/operation staff information and training | Energy checks, Monitoring |  | Adjust energy performance to user demand
[6 empty] | Cl, AR, EP, DF |  |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF | [6 empty] | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF | [7 empty] | Cl, AR, EP, DF |  | Cl, AR, EP, DF |  | Cl, AR, EP, DF |  |  |  | Cl, AR, EP, DF | Cl, AR, EP, DF |  | Cl, AR, EP, DF
[6 empty] | 101005,103007,403008,203015,403017,100023,103024,101025,312031,207033,112036,207037,206040,313047,405060,213061,313065 |  |  |  | 101001,111002,101003,101005,101012,403013,100023,103024,101025,101026,312028,312031,207033,313047,101053,308054,308059,405060, 101012, 103024 |  |  | 101012,100023,103024,101026,313047,101053,308054,308059,405060, 312031 |  |  | 312031 |  |  |  | 101001,111002,101003,101005,403013,100023,103024,312028,207033,313047,101053,308054,308059,405060, 101012 |  |  | 101026,312031,313047,101053,308054,308059, 100023 | [6 empty] | 101001,111002,101003,101005,403013,100023,103024,101026,312028,207033, 101012 |  |  | 100023,103024,101026,312031 | [7 empty] | 402004,103018,308020,213032,308038,208039,308062, 112036 |  | 312031,308038,208039 |  | 308038,208039 |  |  |  | 308044,308045,400064,300067 | 308044 |  | 308044,400064
[6 empty] | T02101 |  |  |  | T02101,T02201 |  |  | 0 |  |  | T04101,T05301,T05201 |  |  |  | T02201 |  |  | T02201,T02103 | [6 empty] | T02201 |  |  | T02201, T02203 | [7 empty] | 0 |  | 0 |  | 0 |  |  |  | 0 | 0 |  | 0
E
[16 empty] | E010 | [9 empty] | E020 | [8 empty] | E030 | [5 empty] | E060 |  |  | E040 |  |  |  |  | E070 |  | E050
[7 empty] | 0 | [8 empty] | Preliminary design approach | [9 empty] | Concept design'approach | [8 empty] | Design development approach | [5 empty] | Contractirng |  |  | Construction works |  |  |  |  | Occuppation |  | Operation
0
[16 empty] | Cl, AR, EP, DF | [9 empty] | Cl, AR, EP, DF | [8 empty] | Cl, AR, EP, DF | [5 empty] | CL, PM, AR, SE, ME, EL, CE |  |  | Cl, AR, EP, DF |  |  |  |  | BO, BM, T, UO |  | Cl, AR, EP, DF
[16 empty] | 213046 | [9 empty] | 100019 | [8 empty] | 100019 | [5 empty] | 213032 |  |  | 308059, 308062 |  |  |  |  | 308045 |  | 308045, 308044, 308048, 308049
[16 empty] | T04224,T04223 | [9 empty] | T01104 | [8 empty] | T042510, T042516 | [5 empty] | 0 |  |  | 0 |  |  |  |  | 0 |  | 0
| F | Formal result / documents
|  |  |  | F010 |  |  | F020 |  |  | F030 | [5 empty] | F040 |  |  |  | F050 | [5 empty] | F060 |  |  |  | F070 |  |  |  |  | F080 |  |  | F090 |  |  | F100 |  |  |  |  | F110 |  |  | F120 |  |  |  | F130
|  |  |  | Contracts and safeguard financing |  |  | Project definition report |  |  | Building program requirement profile | [5 empty] | Pre-design report |  |  |  | Renewed / specified building programme performance profile | [5 empty] | Concept design report |  |  |  | Centred requirements performance profiles |  |  |  |  | Design development report building documents |  |  | Confirmed performance profiles |  |  | Buildings contracts |  |  |  |  | Commiss. report certificat. of build. |  |  | Lease/use contract |  |  |  | Changes in building use
|  |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF | [5 empty] | Cl, AR, EP, DF |  |  |  | Cl, AR, EP, DF | [5 empty] | Cl, AR, EP, DF |  |  |  | Cl, AR, EP, DF |  |  |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  |  |  |  | Cl, AR, EP, DF |  |  | Cl, AR, EP, DF |  |  |  | Cl, AR, EP, DF
|  |  |  | 311006,103007,203015,403017,101025,207033,313047,405060 |  |  | 101005,311006,103007,403008,111009,413010,213011,203015,403017,100019,101025,312029,207037,206040,307041,213042,213043,312050,312052,213061,313065, 103007 |  |  | 101005,311006,103007,403008,111009,413010,213011,203015,413016,403017,100019,111027,312028,312029,207037,206040,307041,213042,213043,312050,312052,313065 | [5 empty] | 100019,207037,206040,213061 |  |  |  | 101005,103007,403008,111009,413010,213011,203015,413016,403017,100019,111027,312028,312029,207037,307041,213042,213043,213046,312050,312052,300056,313065 | [5 empty] | 100019,207037 |  |  |  | 100019,111027,312028,312029,207037 |  |  |  |  | 100019,207037 |  |  | 100019,112036,207037 |  |  | 112036 |  |  |  |  | 308034,300035,308048,313057 |  |  | 0 |  |  |  | 312029
|  |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0 |  |  | 0 |  |  |  | 0
| G | Transmission decision steps client
[6 empty] | G010 |  | G020 | [8 empty] | G030 | [9 empty] | G040 | [8 empty] | G050 |  |  |  |  | G060 | [5 empty] | G070
[6 empty] | First project initiative |  | Design start-up decision | [8 empty] | Pre-design decisions | [9 empty] | Concept design'decisions | [8 empty] | Definitive design decisions |  |  |  |  | Buildings contract decisions | [5 empty] | Building use/rent decisions
0
0
[6 empty] | Cl, AR, EP, DF |  | Cl, AR, EP, DF | [8 empty] | Cl, AR, EP, DF | [9 empty] | Cl, AR, EP, DF | [8 empty] | Cl, AR, EP, DF |  |  |  |  | Cl, AR, EP, DF | [5 empty] | Cl, AR, EP, DF
[6 empty] | 103024 |  | 111027,405060, 103024, 103007 | [8 empty] | 111027, 103024 | [9 empty] | 111027, 103024 | [8 empty] | 111027, 103024 |  |  |  |  | 112036, 103024 | [5 empty] | 103024
[6 empty] | T02201 |  | 0 | [8 empty] | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0

## Actors
Actors List
Name | Nr | Actor | Role
CL | 1 | Client
IN | 2 | Investor | Provide all or part of financing
DV | 3 | Developer | Manage the process of site acquisition, project development, design & construction
O | 4 | Owner | Own all or part of the building; could also be investor or developer or buy later.
PM | 5 | Project manager | Retained by developer to organize whole process, incl. site and project development, design & construction
RO | 6 | Regulatory officer | Represents local authority in interpretation of regulations
DT | 7 | Design Team
AR | 8 | Architect | Professional architect, usually in charge of overall design process
EP | 9 | Energy planner | Supports improved energy performance by proposing design approaches to design team
SE | 10 | Structural engineer | Designs the building structure
ME | 11 | Mechanical engineer (HVAC) | Designs HVAC and plumbing systems
EL | 12 | Electrical engineer | Designs electrical systems
BS | 13 | Building envelope specialist | Assesses features & proposes measures to improve building envelope performance
CE | 14 | Civil / Services engineer | Designs infrastructure, such as sewers & roads on site
GE | 15 | Soils Engineer / Geologist | Assesses site for soil and foundation issues, undertakes remedial action
LD | 16 | Landscape designer | Designs site improvements and landscaping
ID | 17 | Interior designer | Designs interiors, especially in retail or office buildings; usually directly for tenants
DF | 18 | Design facilitator | Facilitates the design process through management techniques
QS | 19 | Quantity surveyor / Cost consultant | Calculates quantitities and costs
ES | 20 | Energy simulator | Undertakes energy simulations
DS | 21 | Daylighting specialist | Assesses features & proposes measures to improve daylighting performance
LS | 22 | Lighting specialist | Designs artificial lighting systems, for architect and/or for tenants
AS | 23 | Acoustic specialist | Assesses features & proposes measures to improve acoustics & reduce noise
CS | 24 | Controls specialist | Designs automated building control systems
TS | 25 | Telecom specialist | Designs building telecom systems
MS | 26 | Eco / materials specialist | Assesses features & proposes measures to improve environmental performance of building materials
ELE | 27 | Elevator / escalator specialist | Designs building elevator and/or escalator systems
FS | 28 | Fire specialist | Assesses features & proposes measures to improve building fire safety performance
OS | 29 | Other specialist | Could include specialists in retail, hotel, hospital design etc., or other specialized technical system.
AS | 30 | Architect site supervisor | Supervises construction on behalf of architect
SS | 31 | Specialist site supervisor | Supervises construction / installation of a specialized system
CS | 32 | Construction site supervisor | Supervises construction on behalf of contractor
GC | 33 | General contractor | Main contractor, who uses sub-contractors
C | 34 | Contractor
SC | 35 | Sub-contractor | Specialized contractors retained by general contractor
PM | 36 | Building products manufacturer | Producer and vendor of building materials or manufactured products
CA | 37 | Commissioning agent | Designs and executes commissioning plan, to ensure that design intent is fulfilled
BO | 38 | Building operator | Responsible for overall operation of the building, on behalf of the owner
BM | 39 | Building operating & maintenance staff | Responsible for routine operations and maintenance
T | 40 | Tenant | Responsible for lease for all or part of a building
UO | 41 | User / Occupant | Uses the spaces within a building, either as a worker, resident or visitor

## Issues
INDEX (ID n°) | L1 | p1keyissue | KID | Problem | bspE | Reason1 | Reason2 | Reason3 | Impact1 | Impact2 | Impact3 | Solution1 | Solution2 | Solution3 | Issue Related Problem 1 | Issue Related Problem 2 | Issue Related Problem 3 | Reason 1 | Reason 2 | Reason 3 | Impact 1 | Impact 2 | Impact 3 | Recommend. Solution 1 | Recommend. Solution 2 | Recommend. Solution 3
100019 | 1 | 0 | 19 | Interim results and decision making in the process |  | Actors possibly pursue own interests, which are not disclosed to the team | Lacking leadership qualities of the team leader. |  | The trust relationship in the team is disturbed. | Confusion about further development of design. |  | Intervention of the team leader or the client to find the facts.
100021 | 1 | 0 | 21 | Operating staff competence and interest in the building performance monitoring. |  | Requirements and interrelations are not sufficiently explained during the personnel's education. | Selection criterions for the personnel are not sufficiently specific. |  | The building monitoring doesn't allow to assess the building concept. | Possibilities to the optimization of the building use are not recognized and are not identified |  | Develop specifications which allow the client to select the building operators by relevant criteria. | Ensure a proper transition and training period for the building operator staff. | Develop monitoring concepts with a low chance for errors.
100023 | 1 | 0 | 23 | Changes of the roles and functions of engineers and architects in recent times |  | Reason1: Demand for more wholistic and complex services; Reason2: Increasing complexity in designing and realization tasks. | Prepare individual contractual agreements between client, architects and engineers | Consistently keep up further education duties.
101001 | 1 | 1 | 1 | Actors key competences in such area like energy,environment or management are insufficient |  | Minimal further education. | Post education not relevant to the main topics |  | Frustration and tensions among the team members because of the inability to translate the sustainability objectives into concepts | Leads often to a fall back on very conventional solutions. |  | Client deals with lacking competence of the actors by getting more external consulting advice | Complementing the team at an early stage of the process | Consider the possibility of replacing some actors.
101003 | 1 | 1 | 3 | Teamleader management efficacy |  | Reason1: Inadequate training or experience level for team management.; Reason2: The teamleader is overburdened with addional tasks; Impact1: Structural and organizational difficulties hamper the essential team work | The client should consider how his structure can help overcome the problem | Relief by delegation of partial tasks to external actors.
101005 | 1 | 1 | 5 | Consensus level on sustainability goals. |  | Reason1: Every actor only argues on the basis of his subject-specific view.; Reason2: The design task is not sufficiently detailed.; Impact1: Engineers and architects developing solutions which do not match | Change the team in its composition. | Set up a documented agreement which serves as a reference to all actors and can be revised if necessary | Provoke discussions within the team until a real agreement is reached |  | 101005_2 |  |  | 101005_2 |  |  | 101005_2 |  |  | 101005_2
101012 | 1 | 1 | 12 | Availability of external experts during early design phases. |  | By lack of motivation as well as lack of basic investigation, the basis to involve external experts is missing. | Despite previous positive experiences, It is not yet common to have an external support advice during the early design stage |  | Design process starts on inadequate prerequisite | Missing essential sustainable project goals. |  | Architect and/or other actors should argue with the client about the necessity of getting qualified external advice
101022 | 1 | 1 | 22 | Uncontrolled changes in team composition during the course of the design and realization process. |  | Changes of project goals or priorities. | External influences lead to new basic design conditions. |  | Irreversible decisions are taken without having scanned all the possible solutions. | Design solutions change in a more conventional direction and are no longer based on the innovative building or energy concept. | Delay and information loss in the design process. | Fix contractually the involvement of the actors as per the design and realization stages
101025 | 1 | 1 | 25 | Inclusion of engineers and architects into early design process. |  | Reason1: Due to time and financial constraints, it is rare that energy/environment consultants are hired by the client at the very early stages.; Reason2: Tight budget prevents the involvement of additional experts.; Impact1: Unsatisfactory design and implementation. | Early inclusion of environmentally qualified experts in the process has a very high payback
101026 | 1 | 1 | 26 | Psychological impact on core team because of inclusion of outsiders |  | Reason1: Additional experts are often seen primarily as competitors and not as acting positively for the project.; Reason2: The contractual relations are in this case not often clear enough; Impact1: Additional tensions in the team hinder the project to progress effectively | Let the team know (contractually too) that a negative attitude in the cooperation may lead to the exclusion from the project. | Explain with great detail the advisor's role to all team members - especially the objectives and contractual aspects.
101053 | 1 | 1 | 53 | Contractor resistance to adoption of new technologies and practice |  | Reason1: Contractors do not generally like to work on projects in which technologies are new to them; Impact1: Solutions are either changed in their implementation or poorly implemented | Apply very strict qualification rules for the entreprises.
103007 | 1 | 3 | 7 | Willingness of the client to support an environmentally conscious design |  | Cost aspects exclusively dominate the planning decisions. | A so tight time frame prevents for an environmentally friendly a design process |  | Demotivation of the design team. | There no chance for the team, even if it is self driven and motivated, to design a successfull building. |  | The client and the architect should first agree on the importance of energy/environmentally conscious design process. | An external and independent advisor should be hired by the client and assist the client and architect to select the design team accordingly.
104056 | 1 | 4 | 56
103018 | 1 | 3 | 18 | Cooperation of entreprises for environmental goals |  | Reason1: Interdisciplinary cooperation is not yet state of the art.; Impact1: Ambitious projects fail because of the imperfect realization of the concept | Develop very detailed and stringent specifications, which force the contractors to take care. | Inform and try to motivate the contractors and if necessary add specific clauses in the contracts.
103024 | 1 | 3 | 24 | Confrontation and conflict of interest |  | Reason1: Actors are not in the adequate technical or contractual position in order to remove the conflicts.; Reason2: Individuals have conflicting goals and/or interests in their mandate; Impact1: It is likely that hidden agendas of some team members drive the design process in an inadequate direction. | When selecting the design team's, potential conflicts of interest must be considered as a selection criterion. | Use the MCDM Method to sort out conflicts of interest.
111002 | 1 | 11 | 2 | Interdisciplinary and communication skills do not correspond to the project reqirements. |  | Reason1: Until now, such skills were not asked to the actors.; Reason2: Actors experiences and main activity focus are one-sided - either theoretical or practical.; Impact1: The lack of interdisciplinary knowledge doesn't allow the team to develop the most appropriate solutions. | Intensify communicative and technical inclusion of the relevant actors |  |  | specifi comments
111009 | 1 | 11 | 9 | Communication problems due to different background leading to different use of concepts and definitions. |  | Reason1: International composition of the design- and realisation team.; Reason2: Very different background and fields of activity; Impact1: Continuous misunderstanding on used terms possibly leading to inconclusive work and later fall back to conventional solutions. | Development of a comprehensible glossary as common communication platform for each participant | Develop and use more pictorial and graphic communication means.
111014 | 1 | 11 | 14 | Engineers ability to present and argue their design concepts |  | Different subject-specific point of views and priorities of the actors. | Engineers have not been trained enough in arguing on a high abstract level |  | Architects and client initiate the initial design process without inputs from engineers | Design solutions have to be found by the engineers as "retrofit" and not as integrated solutions |  | Develop team management techniques to assist engineers in describing their concepts | Consider and get process moderation to ease the discussion
111027 | 1 | 11 | 27 | Degree of transparency in client decision-making |  | Reason1: Client structure does not allow transparent and predictable decision making; Impact1: Lacking security for the designers and weakened trust.; Impact2: The extra work load due to changes has not been discussed and is therefore felt as unjustified. | Changes have to be discussed with all concerned actors as well as their consequences | Use the MCDM-Method.
112036 | 1 | 12 | 36 | No assignment for execution drawings by direct contract to a general entreprise |  | Saving of planning costs | Short design and realisation duration without much consideration for sustainability aspects |  | No consideration of energy- and resource efficient system solutions. | Low quality of built solutions with the possible need of retrofit later |  | Make the clients conscious about to this aspect. | Pay extra attention on supervision and quality management.
203015 | 2 | 3 | 15 | Client acceptance of energy efficient and innovative design concepts |  | Reason1: Refusal on the basis of superficial cost arguments.; Reason2: Client equating innovation with risk; Impact1: Team members loose their motivation and fall back on easier and more conventional design solutions | Try to explain innovations as a way to get answers to design questions, and not just per se | Visit "successful" buildings and talk to satisfied users.
206040 | 2 | 6 | 40 | Effect of time constraints on sustainability goals |  | Reason1: Important dates must be kept.; Impact1: Already initiated concepts development must be discarded, or stopped. | Reduction of ambigous goals which can be reached then within the given time budget.
207033 | 2 | 7 | 33 | Adequacy of budget for additional supervision during execution. |  | Reason1: New building concepts and related systems components need detailed supervision.; Impact1: Ambitious concepts fail because of inadequate supervision | Identify as early as possible specific requirements for execution of non standard systems/components. | Check again negotiation possibilities with the client.
207037 | 2 | 7 | 37 | Vulnerability of energy relevant components to building budget constraints |  | Budget constraints lead to a reassessment of the design solutions |  |  | Ambitious design goals become obsolete. | By the "leaving out" of certain components inadequate results can occur. | All "superfluous" and "dispensable" components of the design concept are suppressed | Use methods like MCDM-method (Multi-Criteria-Decision-Making) before sacrifice of high energy performance solutions. | Discuss cost saving and shifting strategies between investment, running and maintenance cost.
208039 | 2 | 8 | 39 | Subsitution of substandard components in place of original bid specifications |  | Reason1: In the price pressure on components enterprises try to substitute specified items with other cheaper material, components; Impact1: Quality losses occur with effects on the longevity and the daily use of building components or systems. | Provide stringent comparison procedure and very tight specifications for performance of components. | Includeunambiguous quality reqirements consistently into bids.
213011 | 2 | 13 | 11 | Weighting (relative importance) of the energy - and sustainability related goals not specified |  | Reason1: Inappropriate priorities already specified during the task definition.; Reason2: External forces are in contradiction to sustainability concepts and goals.; Impact1: Over or undersizing of systems and/or installation of additional system/components. | Evaluate and compare carefully the building programme and the environmental requirements. | Analysis of the building and energy concept (simulation tools) and identification of the weak points
213032 | 2 | 13 | 32 | Realisation of sustainable project goals with Total- or General-Contractors. |  | Reason1: Total- or General-Contractors do not all have fundamental energy and environmental related knowledge.; Reason2: Priority cost driven design of General- or Total-Contractor.; Impact1: In wide areas of the building sector, sustainability goals are poorly marketable because of structural causes. | Choose candidate contractors with external assistance. | Hire external energy advisor to accompany the process.
213042 | 2 | 13 | 42 | Weak definition of sustainablity goals. |  | Reason1: Definition of performance goals requires a general culture and experience of the design team which is not always available.; Impact1: Difficulties with the implementation of "weak" criterions into actual design process | Visit similar buildings to collect actual numbers and facts. | Study guidelines to get some reference values. | Detailling of goals during the design progress and revision if necessary.
213043 | 2 | 13 | 43 | Extreme comfort requirements lead to overzing of heating and cooling systems. |  | Exaggerated and not controlled ideas of the client or the user. | Unflexible laws and rules. | Exaggerated security margin in design | Oversized plants and therefore high investments and operation cost. | Discrimination of naturally supported systems against purely mechanical driven plants. |  | Explain the interrelation between requirements, investment and operation costs to the client. | Discussion with the users to better understand actual comfort requirements
213046 | 2 | 13 | 46 | Design for flexible building utilization against optimized and sustainable building and installation concepts. |  | Reason1: Client / Designer do not know about future building users and their requirements.; Impact1: By fear of lack of flexibility, high performance systems are rejected. | Develop precise requirements by use of simulation tools. | Assess carefully flexibility needs against design solutions and constraints
213061 | 2 | 13 | 61 | Constraints and limitations by building code regulations are in conflict to sustainable project goals. |  | Reason1: In some situations, technical regulations do not allow the development of energy efficient solutions; Impact1: Solutions rejected only on the basis of regulations | Develop an argumentation based on a solid technical dossier and use existing leeways to make a first case.
300035 | 3 | 0 | 35 | Completeness of service handbooks for buildings and systems |  | In many innovative projects, contractors are not in a position to explain the functionality of systems in relation to the design concept | Details and specifications for the systems use in operation are only partially developed by the designers |  | Service handbooks missing | The operators understanding of functional interrelations in the building is not developed |  | Specify that the the coordination and control of quality and completeness of operation manuals appears in the engineers contracts.
300056 | 3 | 0 | 56 | Changes made to systems after construction alter the intended interaction between building/systems and systems |  | Reason1: Users expectations regarding comfort changed.; Impact1: The change of requirements generates a chain of further necessary interventions and adaptations. | Perform analysis of the interactions of additional components before the intervention into the working system is performed
300066 | 3 | 0 | 66 | Insufficient specification of the building envelope in tendering documents. |  | Costs and time pressure during specifications for tender. | Excessive confidence in manufacturers. |  | Actual envelope has much higher transmission and air infiltration losses than planned. | Expensive updates. |  | Specify and implement checking of envelope quality be testing (e.g. building under pressure and leak measurment)
300067 | 3 | 0 | 67 | Natural or hybride ventilation systems often wrongly operated. |  | Reason1: Users not properly informed or not motivated to operate the system.; Impact1: Indoor climate of the building is unsatisfactory. | Motivation and follow-up of the users especially at early stages of the building occupancy.
307041 | 3 | 7 | 41 | Lack of extensive studies at preparatory stage of the design (environmental study, environmental compatibility examination). |  | Extensive studies in the Predesign phase delay the construction and utilization | New findings and results from the studies can give unexpected turns to the design process. |  | The lack of environmental studies does not allow a qualified selection and building positioning on the site. | Design related basic data and facts will be recognized too late. There is no chance of integration into current design concept. |  | Examination of the synchronization between studies and design process. | Set the environmental studies in relation to the building programme and requirements
308020 | 3 | 8 | 20 | Specific study for cost estimation of innovative design solutions. |  | Reason1: For many innovative system solutions, assessment cannot be based on catalogs or empirically established figures; Impact1: Uncertainty on the budget estimate by lack of detailed analysis (sizing and costing) | Try to get actual cost figures and technical problems of already existing similar systems. | Get a potential supplier or enterprise to offer the development of a realistic costing of the solution.
308034 | 3 | 8 | 34 | Level of importance given to energy relevant aspects during building commissioning and checking of those |  | Reason1: The user has many other priorities during commissioning than energy.; Reason2: A functional check and perhaps the related corrections were not explicitly assigned; Impact1: HVAC-Systems and other energy related systems are commissioned suboptimally or don't perform as planned | The comissioning of systems and/or installation should be specified and assigned explicitly as a task in contractual form
308038 | 3 | 8 | 38 | Quality control during execution. |  | Enterprises not conversant with realisation details or important quality issues. | Inadequate staff provision to the sufficient perception of the control function. | Contractors try to mask mistakes during implementation consciously. | Important details while executing may have an impact on the performance of the components/systems and consequently on the building performances |  |  | Intensive detailling and exhausting description of energy-relevant building parts. | Motivation of the craftsperson through an appropriate inclusion into the design and the design concept.
308044 | 3 | 8 | 44 | Lack of monitoring of real energy consumption values against design or simulation values. |  | Reason1: The building doesn't attain the originally planned performance.; Reason2: A possible optimization of building use is excluded upfront by the client; Impact1: Existing optimization potentials are not implemented | Install a building energy management system which allows regular performance analysis. | Specifiy the monitoring task as a contract item for the building operating staff. | Train the building operating staff
308045 | 3 | 8 | 45 | Inadequate specification and selection process of building operator. |  | Reason1: Requirements upon the use of High performance Buildings are not considered as criteria for the operator selection.; Impact1: The selected building operator does not have the knowledge to manage efficiently the building energy related aspects | Definition of exclusion criterias, which deal with the qualification of the enterprise as well as of its staff | Prepare a competitive bidding for building operation concept
308048 | 3 | 8 | 48 | Partial commissioning of systems/components with testing, measurment of power measurment not possible |  | Reason1: Different level of the completion between separate disciplines; Impact1: Deficiencies occur after final comissioning or even become visible only during utilization. | Optimisation and synchronisation of individual partial commissioning | Provide incentives and further advantages in connection with building labelling and certification.
308049 | 3 | 8 | 49 | Lack of analysis (measurment) of seasonal influences on naturally supported HVAC systems |  | Reason1: Commissioning and testing of naturally supported HVAC-systems cannot be performed at once because of the seasonal differences.; Reason2: Long monitoring periods to assess seasonal influences is not accepted.; Impact1: Seasonal unsteady performance of the HVAC-Systems because of incomplete adjustment of seasonal parameters | Develop a schedule for testing of system behaviour for the various typical seasonal conditions.
308054 | 3 | 8 | 54 | Inadequate validation of energy efficient design solutions by lack of comprehensive simulation of the systems |  | Reason1: The simulation of complex systems is expensive.; Reason2: Simulation of complex systems require special competences; Impact1: Comparison and assessment of alternatives solutions are either incomplete or missing for decision making | Inclusion of qualified experts for simulation and analysis tasks. | Development of a common understanding of the assessment methods
308059 | 3 | 8 | 59 | Lacking Quality assurance and control in relation to the energy concept quality |  | Reason1: Without simulation tools, a secured judgment of the energy concepts is possible only after commissioning.; Impact1: Costly and high constraints related modification after commissioning | Use dynamic simulations and other tools to assess the concept design during the process |  |  |  |  | 308059_3
308062 | 3 | 8 | 62 | Development and use of new building components/systems in the frame of the design process. |  | Reason1: Market not able to offer the required systems/components at an affordable price or on time; Impact1: If the new component cannot be sourced, phe project reaches a dead end, and requires substantial modifications; Impact2: Testing and certification of the new components must be performed before commissioning | Abandon risky approach and find alternative safer solutions | Provide a fall-back position on a more conventional system/material in the specifications for tender.
311006 | 3 | 11 | 6 | Insufficient description of the interrelations between the energy systems |  | Reason1: The energy concept is neither described orally nor explicit in the drawings.; Reason2: Contractors tend to choose "easier solutions" in the sense of solutions which are simpler to execute or cheaper.; Impact1: Deviations / lacks with jeopardise the design concept altogether. | Specify and check performance of elements and systems. | Client should be willing to pay for a follow-up by the design team during execution (even in the case of transfer of responsibilities to the contractors)
312028 | 3 | 12 | 28 | Continuity and concistency of project and design knowledge. |  | Frequent actor changes | Parallel project treatment. | Inadequate documentation of the planning processes. | The projectdiverges (qualitatively and quantitatively) from the original design. |  |  | The same actors do accompany the project from the first design studies up to the realisation (this requires some additional financing). | Concepts and decisions must be documented in such a way that they can be understood by new team members at anytime.
312029 | 3 | 12 | 29 | Inadequate documentation of design changes |  | Changes from the execution drawings are not documented | Reports and protocols are regarded as additional burden. |  | It may happen, that solutions which were proposed, analysed and rejected are again introduced in the design. | Poor basis for possible changes later in the building life cycle |  | Improve documentation methods and tools. | Allow sufficient resources for documentation tasks.
312031 | 3 | 12 | 31 | Frequent changes of design basics, requirements or structure during design process |  | Basic legal requirement not checked during the process | The client did not define suitable reqirement profile neither goal catalog for the project. |  | Unclear design basics slow the project design process | Set up of clear targets is held up and delayed. |  | Inform the client about the risks, impacts and consequences of changes on the building performance and -quality.
312050 | 3 | 12 | 50 | Incomplete utilization and functional program. |  | Reason1: The client is not able to specify his requirements with enough detail; Impact1: Fundamental changes, that essentially have an effect on the budget, are likely to occur in a later design or realization phases. | Get the functional programm completed and reviewed before any further process of design is initiated. | Use check lists, user interview and feasibility studies to specify the requirements.
312051 | 3 | 12 | 51 | Incomplete analysis and documentation of basics. |  | Reason1: Application for incentives or subsidies in various programmes, require detailed documentation; Reason2: Meaningful basics and analyses are not performed because of time and financial constraints; Impact1: The planners must substitute unknown basic conditions with assumptions and corresponding security margins | Stress the importance of preliminary studies. It allows to progress faster later in the process | Shifting of some of the studies in following phases with time related consequences
312052 | 3 | 12 | 52 | Inadequate or insufficient documentation of process-relevant optimization steps |  | Reason1: No effective method for the whole team to document the design process is available; Impact1: Refusal of suggested solutions , because they cannot be sufficiently understood by the decision-makers. | Organise and develop a documentation framework at the begining of the project. Discuss also about contractual consequences
313047 | 3 | 13 | 47 | Additional design expenditure of ambitious energy efficient and sustainabilty oriented projects. |  | New solutions are not part of "standard solution" catalogue and therefore require more work to be implemented. | Lacking practiceal experience, and/or difficult access /knowledge about simulation tools. |  | Keeping the project schedule is difficult | Delay in basic design decisions |  | Invest early in design development including simulations and mock-up models to assess various solutions. | Delegation of the simulation tasks to external experts. | Fees for additional work should be discussed in the team and negociated with the client (keeping in mind the other benefits). | as an example of comments
313057 | 3 | 13 | 57 | No update of design documents in spite of structural changes after commissioning. |  | Reason1: Thedesigners don't have any more access to the design documents because they are the property of the client, and no contractual relation exists anymore; Impact1: Uncontrolled changes to the original design leading to muvh higher energy consumption. | Contractual relation with the design team ensuring a follow-up after building commissioning
313058 | 3 | 13 | 58 | Development of a basis to compare and assess alternative design solutions. |  | Reason1: Design solutions which have to be compared are different in their level of development and detailling.; Impact1: Solutions pursued without serious evaluation potentially leading to ultimate failure. | Parallel development of designs variations with the same level of detailling.
313063 | 3 | 13 | 63 | Uncertainty for design margin of innovative, naturally supported HVAC-Systems. |  | Reason1: New design solutions do not have readily available reference values to compare with; Impact1: Due to numerous poorly designed example, there is a risk of an oversizing and possibly the introduction of a redundant system | Evaluation of technical facts of comparable reference installations.
313065 | 3 | 13 | 65 | Multiple functions for one element (e.g. ventilation, shading, lighting, …) are in conflict |  | Reason1: Wrong optimization strategies.; Impact1: Individual element functions overlap each other and cause negative effects on the entire building concept. | Functional schemes must be checked in interdisciplinary and potential conflicts identified |  |  | 312065_3 |  | 312065_3 | 312065_3 |  | 312065_3 | 312065_3 |  | 312065_3 | 312065_3 |  | 312065_3
400064 | 4 | 0 | 64 | Drastically changing internal gains because of users influence. |  | Reason1: Changes of technical infrastructure and equipment in course of project; Impact1: Systems which have been sized according to very tight specifications may not cope with such changes | Oversizing of ventilation systems (natural or mechanical) does not lead to more energy consumption if properly operated
402004 | 4 | 2 | 4 | Contractors reject the guarantee for innovative systems because of lack of reference |  | Reason1: Project design not sufficiently detailed, leaving "grey areas" to the entreprises; Impact1: Client must pay extra costs for entreprise accepted solution or modification | Design must be specified in detail and guarantee explicitly mentioned in the bidding documents.
403008 | 4 | 3 | 8 | Consciousness level for the long-term, structural and spatial impacts on the urban context. |  | Reason1: The client does not have any feeling for the image and impact in the urban context; Reason2: Not enough explicit town-planning requirements and specifications to drive the process; Impact1: Development of inadequate design in regard to the urban context | Establishment of clear design guidelines for the urban integration for buildings in competition procedures. | Develop appropriate guidelines for the design development
403013 | 4 | 3 | 13 | Construction and system costs-related fee structure holds back the work out of alternative design solutions |  | Traditional fee structure doesn`t support the working of number of alternative design solutions for achievement of performance goals | Innovative solutions and simplifications are correlated with reduced fees instead of premium for advanced solutions. |  | Engineers are not inclined to work on numerous alternative solutions. | Engineers often use risks as a reason, not to reduce investments for the building - infrastructure. | Conventional non optimal solutions are likely to be preferred without any verification on its impact on sustainability goals | Explain to the client which advantages he has through the investment in early design phases analysis. | Ensure fees which matches common solutions level even if it`s planned to build simply and thrifty ( if investments are reduced, too).
403017 | 4 | 3 | 17 | No willingness neither feeling for necessity to invest to achieve low running costs. |  | Short-term high yields appear more lucratively than long-term economic advantages. | External environmental costs don't find any consideration by the clients calculation. |  | High financial and technical expenditure for modernization and maintenance | Poor basis for a resale or a renewed rental. |  | Demonstrate to the client (and to the engineers if necessary) that life cycle costs of a building are as relevant indicators than investment. | Systematically document and assess alternative solutions integrating investment and running costs (energy and maintenance). | Change basic conditions of calculation by inclusion of external environmental costs.
405060 | 4 | 5 | 60 | Necessary tasks for the inventory of the building requirement are not sufficiently financially covered |  | Reason1: Standard contracts do not allow sufficient time allocation for the tasks; Impact1: Lacking decision basis for the concept development and assessement | Add specific contractual clauses and resources to allow for required tasks to be performed
409030 | 4 | 9 | 30 | Execution of the builidng programme inventory as pure "documentation", without required expertise |  | Reason1: Financially advantageous execution by students or laymen without sufficient technical instruction or qualification; Impact1: The inventory is inadequate as a basis for the design | In principle, building programme requirement inventory should be executed under direction of the architect.
409055 | 4 | 9 | 55 | Pollutant burdens on the property / in the building are not tested or discovered too late. |  | Reason1: Lacking proof methods for certain pollutants.; Impact1: Healths impairments during construction or later utilization. | Elaborate analysis about the site history
413010 | 4 | 13 | 10 | Lacking of criterions in laws / norms for implementation of sustainability goals in the process of authorization procedures. |  | Reason1: Inadequate assessments of the economic effects.; Reason2: Deregulation trends by authorities; Impact1: Clients, designer and enterprises are not pushed by legal aspects to develop optimal solutions | Promotion of the voluntary realization of sustainability goals through incentives.
413016 | 4 | 13 | 16 | Low acceptance for the integration of technical solutions into the architecture. |  | Reason1: Recent development in material science and its application has increased the number of possible solutions for building envelope components, hvac etc.; Reason2: Architects and other designers have not yet included the technical improvement in their routine practice (e.g. high performance glazings, ..); Impact1: Ambitious energy-saving or solar-technical solutions cannot be realized. | The team should visit some buildings successfully integrating new technologies. | An external advisor may also help in the initial stages to open up the "space of possible solutions".
end
Note on B1: pjabo: L1 élèments: 1 actors, 2 goals, 3 activities, 4 influences
Note on C1: pjabo: p1key relates to the key issues (1-13)

## Methods and Tools
| Methods / Tool Category | Index | Name / Link | Short Description of Purpose / Characteristic | Language | Country of application | Contact person, Address
1 | Information
1.1 | Handbooks | 01101 | Bertelsmann Baukatalog | Building component catalog with contact adresses | G | D | Bertelsmann Verlag, Frankfurt
|  | 01102 | COMPASS elements | Daylighting component catalog | E | CEC | University of Athens
|  | 01103 | Neuffert Design Components | General component specifications | D, E | International
|  | 01104 | Integral Design with building simulation programmes | Application of simulation tools in the integral design process with short descriptions | ? | CH | EMPA Dübendorf, CH
|  | 01105 | Handbook for passive and hybride solar commercial buildings | Basic description of technolgies and concepts for solar commercial buildings | E | International | James & James
|  | 01106 | "Alle Hus er Solfangere" | Solar design of buildings | N | N | NAL, Oslo, N
|  | 01107 | "Glassgårdshåndboka" | Design of atrium buildings | N | N | NAL, Oslo, N
|  | 01108 | Handbook on solar air systems, IEA Tak 19 | Design guidelines, nomogramms, system descriptions | E | International | James & James
|  | 01109 | Schwarz: Ecology in Building (handbook) | Recommendations for building materials | G | CH
1.2 | Product description | 01201 | Gravivent, ADO company | Gravity driven return air cooling device | G, E | D | ADO company, 60210 Frankfurt, Lüfterstrasse 3
|  | 01202 | PVC freies Bauen | PVC free material list for building construction | G | D
|  | 01203 | Ökologische Baustoffe | Ecological recommended material list | G | D | ifib, University Karlsruhe
1.3 | Case Studies /Examples | 01301 | IEA Case Stories Booklet | Example decription of 13 design storeys and buildings | E | International | collected by Esbensen, Kopenhagen DK
|  | 01302 | IEA Task 11 short report (also Norwegian version) |  | E, N | Internat./N
|  | 01303 | IEA Case studies on passive and hybride solar commercial buildings | 55 example buidlings with concept and size descriptions | E | International | James and James, London
|  | 01304 | IEA Case studies on buildings with solar air systems | 20 example buildings with solar air concepts | E | International | ETH Zürich
2 | Guidelines / Checklists
2.1 | Checklists | 02101 | SIA-Checkliste für energiegerechtes, ökologisches Planen und Bauen | Checklist format for energy efficient environmental design | G | CH, D | SIA
|  | 02102 | GRIP veileder | same ????????? | N | N | GRIP, Oslo, N
|  | 02103 | Passivhaus Checklist | Checklist for components and construction of low energy residential buildings | G | D | Passiv Haus Institut, Darmstadt
|  | 02104 | Ökotest ?, Stiftungs-Warentest 12/99 | Material and components test evaluations by journals or institutions | G | D | Stiftung Warentest, Öko-Test
2.2 | Guidelines | 02201 | TOP Team orientiertes Planen | Team-oriented design guidelines for actors and activities | G | CH
|  | 02202 | Building Details Catalogue |  | ?N | N | Byggforsk, Oslo, N
|  | 02203 | Umweltmanagement von Hochbauprojekten | Ducumentation of the design process for ecological | G | CH | Amt für Bundesbauten
|  | 02204 | Energiesparendes Planen im Hochbau | Design criteria for low energy building design | G | D | Hessisches Umweltministerium
|  | 02205 | PVC free products |  |  | D
|  | 02206 | Ökologische Baustoffe | Ecological recommended material list | G | D | ifib, University Karlsruhe
3 | Requirements
3.1 | Laws and regulations | 03101 | Energiesparverordnung | Heating energy demand regulation including process efficiency | G | D
|  | 03102 | Energiegesetze Bund / Kantone |  | G | CH
|  | 03103 | Verordnung Kantone / Gemeinden |  | G | CH
3.2 | Standards | 03201 | DIN 1946 | Design guidelines for mechanical ventilated and cooled spaces | G | D
|  | 03202 | ASHRAE 55 | Thermal comfort | E | US
|  | 03203 | ASHRAE 62 | Indoor air quality | E | US
|  | 03204 | ASHRAE 90.1 | Energy efficiency | E | US
|  | 03205 | Arbeitsplatzverordnung | Regulation of working place environmental conditions | G | D
|  | 03206 | Wärmeschutznachweis | Heating demand documentation for the building owner | D | D | Bundesverordnung
3.3 | Voluntary requirements | 03301 | Energiepass | Heating demand calculation | D | D | Prof.Hauser, Gesamthochschule Kassel
|  | 03302 | Energienachweis oblig. gem. 0602 / 0603 |  |  | CH
|  | 03303 | Blauer Enge Label | Blauer Engel label for environmental friendly products | D | D
|  | 03304 | "Svanemerket" |  |  | N
|  | 03305 | Passive Haus Komponenten Label | Prooved component for the passive house concept | G | D | Passiv Haus Institut, Darmstadt
4 | Evaluation support
4.1 | Assessment | 04101 | GBC | Green Building Challenge, GBC | E | CA / Internat. | Nils Larsson / Ray Cole
|  | 04102 | BREEAM |  | E | UK
|  | 04103 | LEED |  | E | USA
|  | 04104 | Ecopro | Building material embeded energy evaluation | G | D | ifib Karlsruhe
|  | 04105 | Økoprofil |  | N | N | GRIP, Oslo, N
|  | 04106 | Legoe | Design and evaluation support
4.2 | Simulation and analytical tools
4.2.1 | Visualisation and shading studies | 04211 | Sombrero | Hourly shading profile for free defined area | G | D | Universität Siegen
|  | 04212 | Sunorb | Estimation of shading, overhangs by sun position
4.2.2 | Steady state building evaluation | 04221 | EBSYS | Energy consultance tool | G |  | Forschungsgesellschaft Joanneum, Institut für Informationssysteme und Institut für Energieforschung
|  | 04222 | WBi832 | Calculation of LEK values | G | AU | new version in progress
|  | 04223 | LESOSAI | Monthly energy balances, passive solar systems | E, F, G | CH | EPFL, Leso Institut, Lausanne
|  | 04224 | ARCHPASS | Monthly energy balances, | E | D | TRANSSOLAR Energietechnik GmbH Nobelstr. 15, D-70569 Stuttgart, http://www.transsolar.com/indexarch.htm
4.2.3 | Thermal systems | 04231 | TSOL | Instationary solar thermal systems for DHW and process heat | G | D | Dr.-Ing. Gerhard Valentin, Köpernickerstr. 9, D-10997 Berlin, Tel: +49-30-617917-80 Fax: +49-30-617917-11 http://www.tsol.de/
|  | 04232 | POLYSUN | Dimensioning and energy output simulation for solar thermal systems | G | CH | Arbeitsgemeinschaft ERNEUERBARE ENERGIE, H.v. Türlin Strasse 5, A-9500 Villach, Tel. +43 (04242) 23224, Fax +43 (04242) 23224-1, http://www.datenwerk.at/arge_ee, email: arge-ee-vi@net4you.co.at, http://www.solarenergy.ch/SPF/
|  | 04233 | SHW | Solar heating and domestic hot water |  | AU | Institut für Wärmetechnik, TU Graz; o. Univ. Prof. Dr. techn. D.I. Wolfgang Streicher, http://www.bmwf.gv.at/6extern/forschungsforum/e/sonproj.htm#shw, http://wt.tu-graz.ac.at/
4.2.4 | PV system | 04241 | PV-chart | Evaluation tool for photovoltaic systems |  | D
4.2.5 | Dynamic building load simulation | 04251 | BLAST | Building Loads Analysis and System Thermodynamics |  | USA | Building Systems Laboratory, http://www.bso.uiuc.edu/blastmain.htm
|  | 04252 | DOE-2 | Department of Energy |  | USA | National Energy Software Center, http://simulationresearch.lbl.gov/
|  | 04253 | SUNCODE, SERIRES | SERI Residential Energy Software |  | USA | Mainframe Version: Energy Science and Technology Software Center P.O. Box 1020, Oak Ridge, Tennessee; Suncode – PC 5.7: Kaija Berleman, Ecotope, Inc; 2812 East Madison Street, Seattle, Washington
|  | 04254 | DEROB-LTH | Dynamic Energy Response of Buildings |  | DK | Technische Hochschule Lund, http://lthbkl.bkl.lth.se/derob.htm
|  | 04255 | SMILE | Research Development |  | D | TU Berlin, Institut für Energietechnik, http://buran.fb10.tu-berlin.de/Energie-technik/EVT_KT/smile/
|  | 04256 | SMILE | Dynamic cooling load calculation following VDI 2078, single zone model |  | D | TRANSSOLAR Energietechnik GmbH Curiestr. 2, D-70569 Stuttgart, http://www.transsolar.com/indexcal.htm
4.2.6 | Dynamic building load simulation | 042510 | WAEBED | Calculation of the heating demand |  | AU | Institut für Hochbau, TU Wien, Dipl.-Ing. Dr. Klaus Krec, http://www.baustudio.com/credits/bsaref2.htm
|  | 042511 | GEBA | Summer behaviour, heating load and demand calculation tool |  | AU | Büro für Bauphysik, Schönberg am Kamp Wien, Dipl.-Ing. Dr. Klaus Krec, http://www.baustudio.com/credits/bsaref2.htm
|  | 042512 | Program pakage TWDWI | Heating demand calculation |  | AU | Institut für Wärmetechnik, TU Graz; o. Univ. Prof. Dr. techn. Dipl.-Ing. Hermann Halozan, o. Univ. Prof. Dr. techn. Dipl.-Ing. Wolfgang Streicher
|  | 042513 | ENERGY 10 | Energy, daylighting evaluation and optimisation tool |  | USA | Sustainable Buildings Industry Council und NREL, http://www.sbicouncil.org/enTen/index.html, http://www.nrel.gov/buildings/energy10
|  | 042514 | DK–SOLAR | dynamisches Simulationsprogramm |  | D | Delzer Kybernetik, Ritterstr. 51, D-79541 Lörrach
|  | 042515 | TAS | Thermal Analysis Software |  | UK | EDSL (Enviromental Design Solutions Limited); Ifes (Institut für angewandte Energiesimulation und Facility Management GmbH), http://ourworld.compuserve.com/homepages/eds, http://www.ifes-frechen.de/pages/seiten/soft.htm
|  | 042516 | TRNSYS 15.1 | A Transient System Simulation Programm for systems and buildings |  | USA | TRANSSOLAR Energietechnik GmbH Nobelstr. 15, D-70569 Stuttgart, http://www.trnsys.de/, http://sel.me.wisc.edu/trnsys
|  | 042517 | BSim2000 | Building simulation tool |  | DK | Danish Building Research Institute Postboks 119, DK-2970 Horsholm Dänemark, Tel: +45-4286-5533, Fax: +45-4286-7535, http://www.sbi.dk/English/Publishing/Software/BSim2000/Mainmenu.htm
|  | 042518 | HELIOS-PC | Single zone building simulation tool |  | CH | econzept Energieberatung GmbH, Wiesentalstr. 29, 79115 Freiburg; Tel: 0761/4016627, http://www.econzept.com/
|  | 042519 | ANSYS/FLOTRAN | Finite element calculation method mainly used for construction issues, with thermal bridge evaluation application |  | D | CAD-FEM GmbH, Marktplatz 2, D-85567 Grafing, Tel: ++49 (0)8092-7005-0, Fax:: ++49 (0)8092-7005-77, http://www.ansys.com/, http://www.cadfem.de/software/ansys/ansys1.htm
|  | 042520 | Energi i bygninger |  |  | N | Skarland Press, N
|  | 042521 | FRES |  |  | N | Skarland Press, N
|  | 042522 | Trnslite | Thermal simulation tool |  | D
4.2.7 | Daylighting | 04261 | Radiance | Detailled daylighting simulation tool with photorealistic output |  | USA | LBL Daylighting group,
|  | 04262 | Superlite | Simplified daylighting evaluation tool |  | USA
4.2.8 | Fluid dynamics | 04271 | Flovent | Simplified fluid dynamic simulation, finite volume method |  | USA
|  | 04272 | Fluent | Detailled fluid dynamic simulation tool, finite volume method |  | USA
|  | 04273 | FIDAP | Detailled fluid dynamic simulation tool, finite element method |  | USA
|  | 02474 | Comis 3.1 | Network fluid flow model
4.3 | Test methods | 04301 | Blower Door Test | Building tightness test method |  | International
|  | 04302 | Thermographic Analysis | Infrared photographie for identifying thermal bridges and leeks |  | International
|  | 04303 | PASSYS facade tests | Outdoor test facilities and test methods for facade systems |  | D | University Stuttgart, Institut für Thermodynamik und Wärmetechnik
|  | 04304 | k-Wert Messung nach DIN ???? | Laboratory test method to determine the thermal U-value | G | D
5 | Design Process Support
5.1 | Communication platform | 05101 | Intesol | Organisation platform for information exchange in the design process | G | D | ifib Karlsruhe
|  | 05102 | Internet project pages | Information exchange on project specific web pages | E | USA | Cephrem Inc.
5.2 | Management and Structuring | 05201 | Mindmapper | Structure drawing program for structuring porcesses, informations and interrelations | E | USA | SimTech Systems Inc., E-mail: simtech@star.elim.net
|  | 05202 | Mindmanager, Superbrain
|  | 05203 | Niku portfolio
5.3 | Decision support | 05301 | MCDM 23 | Computer tool for multi criteria decision making | E | International | SimTech Systems Inc., E-mail: simtech@star.elim.net
|  | 05302 | QFD | Decision making support tool | E | Fin. | VTT, Finland

## Matrix
|  | A |  |  |  |  | B |  |  |  |  | C |  |  |  |  | D |  |  |  |  | E |  |  |  |  | F |  |  |  |  | G
| Label | Activity / Subject | Actors | Issues | Tools | Label | Activity / Subject | Actors | Issues | Tools | Label | Activity / Subject | Actors | Issues | Tools | Label | Activity / Subject | Actors | Issues | Tools | Label | Activity / Subject | Actors | Issues | Tools | Label | Activity / Subject | Actors | Issues | Tools | Label | Activity / Subject | Actors | Issues | Tools
10 | A010 | Rough cost estimate | AR, RO, OS, CS, C | 213011,308020,207037 | T03101,T03102, T042510, T042511, T042512 | B010 | - Project brief - Objectives - Background - Influences | Cl, AR | 409030 | T01301,T01303 | C010 | Programme demand and requirements | Cl, AR, EP, DF | 101012,312050 |  | D010 | First design advice | Cl, AR, EP, DF | 101005,103007,403008,203015,403017,100023,103024,101025,312031,207033,112036,207037,206040,313047,405060,213061,313065 | T02101 | E010 | Preliminary design approach | Cl, AR, EP, DF | 213046 | T04224,T04223 | F010 | Contracts and safeguard financing | Cl, AR, EP, DF | 311006,103007,203015,403017,101025,207033,313047,405060 |  | G010 | First project initiative | Cl, AR, EP, DF | 103024 | T02201
20 | A020 | Consider Building codes, regulations and industry standards | AR, EP, ME | 213061, 103007, 104056, 103018 | T02101 | B020 | - Site inspection - Site analysis | AR, ES, CS, LD, ID, DF | 409030 | T01303 | C020 | Feasibility studies | Cl, AR, EP, DF | 312050,313065 |  | D020 | Set up design team (alternatives) | Cl, AR, EP, DF | 101001,111002,101003,101005,101012,403013,100023,103024,101025,101026,312028,312031,207033,313047,101053,308054,308059,405060, 101012, 103024 | T02101,T02201 | E020 | Concept design'approach | Cl, AR, EP, DF | 100019 | T01104 | F020 | Project definition report | Cl, AR, EP, DF | 101005,311006,103007,403008,111009,413010,213011,203015,403017,100019,101025,312029,207037,206040,307041,213042,213043,312050,312052,213061,313065, 103007 |  | G020 | Design start-up decision | Cl, AR, EP, DF | 111027,405060, 103024, 103007
30 | A030 | - Review goals and requirements - Qualified cost estimation | AR, DV, EP | 308020 | T02203,T04102,T04101 | B030 | Investigation on: - Urban integration - Proportion - Site development | AR, RO, LD | 312050 | T01301,T02203 | C030 | - General dispositions mass/functions - Horizontal/vertical development - Building periphery | Cl, AR, EP, DF | 413016,313058,313065 | T01106, T01108, T01301 | D030 | Call in expert (e.g. jury, …) | Cl, AR, EP, DF | 101012,100023,103024,101026,313047,101053,308054,308059,405060, 312031 |  | E030 | Design development approach | Cl, AR, EP, DF | 100019 | T042510, T042516 | F030 | Building program requirement profile | Cl, AR, EP, DF | 101005,311006,103007,403008,111009,413010,213011,203015,413016,403017,100019,111027,312028,312029,207037,206040,307041,213042,213043,312050,312052,313065 |  | G030 | Pre-design decisions | Cl, AR, EP, DF | 111027, 103024
40 | A040 | - Calculations - Simulations - Quantifications | AR, EP, ES | 308020,207037,308054,313063 | T04271,T04272 | B040 | General approach for energy supply and systems | AR, EP, DF, BS, ES, DS | 213011,111014,308020,213032,213043,308049,308054,308059,213061,313063 | T02101,T02103 | C040 | - System integration - Selection of building components and materials | DT, AR, SE, EP, ME, DF | 413016,313058,313065, 112036 | T04261,T04262 | D040 | Design'alternatives | Cl, AR, EP, DF | 312031 | T04101,T05301,T05201 | E040 | Construction works | Cl, AR, EP, DF | 308059, 308062 |  | F040 | Pre-design report | Cl, AR, EP, DF | 100019,207037,206040,213061 |  | G040 | Concept design'decisions | Cl, AR, EP, DF | 111027, 103024
50 | A050 | - Life cycle analysis - Cost calculation | AR, BO | 308020,207037 | T04104 | B050 | Check Interfaces: - Proportions - Multifunctionality - Flexibility | AR, SE, O, QS, TS, CS, EL | 213046 |  | C050 | Construction documents | AR, SE, ME | 413016,103018,112036,207037,308038,208039,312050,313058,308062,313065,300066 |  | D050 | Set up / complete 'design team | Cl, AR, EP, DF | 101001,111002,101003,101005,403013,100023,103024,312028,207033,313047,101053,308054,308059,405060, 101012 | T02201 | E050 | Operation | Cl, AR, EP, DF | 308045, 308044, 308048, 308049 |  | F050 | Renewed / specified building programme performance profile | Cl, AR, EP, DF | 101005,103007,403008,111009,413010,213011,203015,413016,403017,100019,111027,312028,312029,207037,307041,213042,213043,213046,312050,312052,300056,313065 |  | G050 | Definitive design decisions | Cl, AR, EP, DF | 111027, 103024
60 | A060 | - Detailed calculations - Simulation | ES, AR, SE, DS, LS | 313063, 308054 | T04252 | B060 | Design and gross sizing of system solutions | DT, CL | 213011,111014,308020,213043,308054,313063 | T04252 | C060 | Bidding | AR, ME, EL, BS, MS, AS,CS, SS | 402004,103018,308020,213032,308062, 112036 |  | D060 | Call in expert | Cl, AR, EP, DF | 101026,312031,313047,101053,308054,308059, 100023 | T02201,T02103 | E060 | Contractirng | CL, PM, AR, SE, ME, EL, CE | 213032 |  | F060 | Concept design report | Cl, AR, EP, DF | 100019,207037 |  | G060 | Buildings contract decisions | Cl, AR, EP, DF | 112036, 103024
70 | A070 | Construction strategies | AR,SE,EP | 103018,213032,101053 | T01110 | B070 | Modular tuning of: - Space use - Construction elements | AR, PM | 111002 |  | C070 | Construction supervision, Cost control, Quality assurance | AS, CS, SS | 308038,208039 |  | D070 | Complete 'design team | Cl, AR, EP, DF | 101001,111002,101003,101005,403013,100023,103024,101026,312028,207033, 101012 | T02201 | E070 | Occuppation | BO, BM, T, UO | 308045 |  | F070 | Centred requirements performance profiles | Cl, AR, EP, DF | 100019,111027,312028,312029,207037 |  | G070 | Building use/rent decisions | Cl, AR, EP, DF | 103024
80 | A080 | Commissioning plan for energy related | AR, ME, DS, LS, CS | 308034,300035,308045,308048,308049 |  | B080 | - Optimise system solutions - Final sizing - System operation | AR, EP, ME, QS | 112036,313063 | T04252 | C080 | Final commissioning | Cl, AR, EP, DF | 308034,300035,308048,308049,313057 |  | D080 | Call in expert | Cl, AR, EP, DF | 100023,103024,101026,312031 | T02201, T02203 | E080 |  | Qualified actors ? |  |  | F080 | Design development report building documents | Cl, AR, EP, DF | 100019,207037 |  | G080
90 | A090 | Operation strategies | AR, BO, CL, QS | 308034,300035,308045,300067 |  | B090 | Environmental criteria and specs for tender | AR, EP, DF, MS, AS, SS, BO | 103018,308020,101053,308059 | T02205,T02206,T02203,T02104 | C090 | Operation manuals | Cl, AR, EP, DF | 100021,308044,308045,400064,300067 |  | D090 | Negotiation | Cl, AR, EP, DF | 402004,103018,308020,213032,308038,208039,308062, 112036 |  | E090 |  |  |  |  | F090 | Confirmed performance profiles | Cl, AR, EP, DF | 100019,112036,207037 |  | G090
100 | A100 | Management and Maintenance plan | BO, MS, BM, QS | 312028, 308049, 308048, 308045 |  | B100 | Requirements upon builders and suppliers, Call for tender | AR, AS, SS, CS, BS | 402004,103018,213032,101053,308059,308062 |  | C100 | Management, Control, Optimisation | Cl, AR, EP, DF | 100021,308044,409055,300056,400064,300067 |  | D100 | Identify and eliminate deficiencies | Cl, AR, EP, DF | 312031,308038,208039 |  | E100 |  |  |  |  | F100 | Buildings contracts | Cl, AR, EP, DF | 112036 |  | G100
110 | A110 | New box example |  |  |  | B110 | Implementation of necessary changes | AR, PM, CL | 409055,300056 |  | C110 | Basics for retrofit design | Cl, AR, EP, DF | 100021,409055,300056 |  | D110 | Operational, functional and energy performance checks | Cl, AR, EP, DF | 308038,208039 |  | E110 |  |  |  |  | F110 | Commiss. report certificat. of build. | Cl, AR, EP, DF | 308034,300035,308048,313057 |  | G110
120 | A120 |  |  |  |  | B120 | Analyse and assess impact caused by project change | AR, QS, CL, DF | 409055,300056 |  | C120 | - Building and energy system - Spatial structure and Construction - Envelope, daylighting, solar - Traffic and HVAC systems | Cl, AR, EP, DF | 413016,313058,313065 | T01106, T01108, T01301 | D120 | User/operation staff information and training | Cl, AR, EP, DF | 308044,308045,400064,300067 |  | E120 |  |  |  |  | F120 | Lease/use contract | Cl, AR, EP, DF |  |  | G120
130 | A130 |  |  |  |  | B130 |  |  |  |  | C130 |  |  |  |  | D130 | Energy checks, Monitoring | Cl, AR, EP, DF | 308044 |  | E130 |  |  |  |  | F130 | Changes in building use | Cl, AR, EP, DF | 312029 |  | G130
140 | A140 |  |  |  |  | B140 |  |  |  |  | C140 |  |  |  |  | D140 | Adjust energy performance to user demand | Cl, AR, EP, DF | 308044,400064 |  | E140 |  |  |  |  | F140 |  |  |  |  | G140
150 | A150 |  |  |  |  | B150 |  |  |  |  | C150 |  |  |  |  | D150 |  |  |  |  | E150 |  |  |  |  | F150 |  |  |  |  | G150
160 | A160 |  |  |  |  | B160 |  |  |  |  | C160 |  |  |  |  | D160 |  |  |  |  | E160 |  |  |  |  | F160 |  |  |  |  | G160
Note on N5: Pierre Jaboyedoff: 'general disposition, mass dispo, functional scheme hor vert development building preriphery
Note on N6: Pierre Jaboyedoff: 'Structural dispositions, frame, room, layout, traffic, space, partition, envelope, daylightning
Note on I9: Pierre Jaboyedoff: Modular coordination: WS,